## Slide 1: Flocculator Design

## Slide 2: Floc model for viscous dominated collisions
Velocity gradient
Initial particle spacing
Flocculation time
Rate constant (model fitting parameter)
A function of fractional surface coverage of particle by coagulant
Particle diameter
Notes: What does the operator control?
What changes in a rain event?
What does the design engineer control?

## Slide 3: Overview
Analysis of hydraulic flocculators
  Vena contracta
  Head loss per bend
  The great transition at =5
Flocculator Design
  Head loss, collision potential, residence time
  Geometry of a baffle space to obtain desired energy dissipation rate

## Slide 4: Top View
W = Width of the flocculator channel
S = Space between baffles
L = Length of a flocculator channel
W
S
L
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 5: Side View
H = Water depth
L = Length of the flocculator channel
S = Space between baffles
T = Thickness of the baffles
B =Perpendicular center to center distance between baffles
H
L
S
1.5S
1.5 S
Upper baffle
Lower baffle
Minimum water level
Port from previous channel
Exit to the sedimentation tank entrance channel
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 6: Design Considerations
The length of the flocculator channels matches the length of the sedimentation tank (thus far…)
Width of the flocculation channel?
  Minimum? ________________
  Material limitations (polycarbonate or concrete)
  Vary to optimize flocculation efficiency (function of geometry)
Need to determine
  Head loss
  Residence time
  Baffle spacing
  Number of baffles
Human width
Notes: planta de 50 Lps con 2 cámaras de sedimentación

## Slide 7: More Design Considerations
Even number of channels for AguaClara design (to keep chemical dose controller near stock tanks), but this may change if flocculators get smaller
Even or odd number of baffles depending on channel inlet and outlet conditions
Begin with the energy source for the turbulence that creates shear that creates collisions: head loss for a baffle

## Slide 8: Vena Contracta around a bend?
Sluice gate (almost closed)*
  0.59
Small hole in a tank
  0.62
Exit from a pipe
  No Vena Contracta
By Lindsay Lally, Lee Hixon (Own work) [CC BY-SA 3.0 (http://creativecommons.org/licenses/by-sa/3.0) or GFDL (http://www.gnu.org/copyleft/fdl.html)], via Wikimedia Commons
* Roberson, JA; Cassidy, JJ; Chaudhry, MH. Hydraulic Engineering. John Wiley. (1995) page 217. Original reference is Henry, H.R. “Diffusion of Submerged Jets.” Discussion by M.L. Alberston, Y.B. Dai, R.A. Jensen, and Hunger Rouse, Trans. ASCE, 115, (1950)

## Slide 9: Vena Contracta (PVC ) Conclusions
Draw the most extreme streamline through the transition and determine the total change in direction
If the change in direction for most of the fluid is 90°, then the PVC is approximately 0.62
If the change in direction for most of the fluid is 180°, then the PVC is approximately 0.622=0.384
Notes: Validation Studies of Fluent Turbulence Models for Fluent Simulations of AguaClara Flocculators
AguaClara Computational Fluid Dynamics Spring 2010
Travis Stanislaus
https://confluence.cornell.edu/display/AGUACLARA/Validation+Studies+for+ANSYS+Fluent+Turbulence+Model+Simulations

## Slide 10: Head Loss coefficient for a Baffle
the contraction coefficient for a sharp 180º bend (0.622)
Head loss in an expansion
We need to measure this in one of the new AguaClara plants!
e - expansion
Notes: Validation Studies of Fluent Turbulence Models for Fluent Simulations of AguaClara Flocculators
AguaClara Computational Fluid Dynamics Spring 2010
Travis Stanislaus
https://confluence.cornell.edu/display/AGUACLARA/Validation+Studies+for+ANSYS+Fluent+Turbulence+Model+Simulations

## Slide 11: Flocculator Efficiency
= 4
= 10
Which space between baffles is better, considering the uniformity of the energy dissipation rate?
This space with very low energy dissipation rate doesn’t contribute much

## Slide 12: Why a transition at of 5?
Jets expand in width at the rate of approximately 1 unit in width per 10 units forward
Expansion length is 10(0.6S)
Expansion requires a distance of approximately 6S
The transition is related to the distance required for the jet to fully expand
0.6S
0.4S
Notes: Flocculators with H/S<5
We need to know what the Baffle head loss coefficient is for this case. It is possible that the head loss coefficient is larger than the 2 that we predict based on the contraction coefficient because the flow will not have fully expanded before going through the next contraction. Thus the head loss is quite possibly higher for the low H/S ratios than what we are assuming. It is important that we figure this out BEFORE we build a large flow plant with a low H/S ratio. We could either obtain a solution using CFD or by conducting laboratory experiments.
It is very likely that the flow fully expands as it goes around the 180 degree bend. Inertia will cause the higher velocity water to move toward the outside of the bend which is where the flow has separated from the baffle. Thus it is quite possible that the head loss is the same for H/S<5 as it is for H/S>5.

## Slide 13: Simplify flocculator design by designing for high efficiency
Efficiency will be a function of the variability of the energy dissipation rate
We expect a relation of the form such that efficiency is 1 when =1 and efficiency is less than 1 for higher values of
We “solve” this unknown by always designing efficient flocculators with 3<H/S<6
S

## Slide 14: Prior to 2015 AguaClara used designs that were far from the optimum
A compact plant layout was possible for small flows by using a vertical flow flocculator with a high ratio
For small plants the width of the channel was determined by the need to construct the channel using humans (45 cm or more)
The space between baffles was very narrow and thus was very high (for low flow plants)
Small plants needed longer residence time and more baffles to achieve adequate flocculation because efficiency was reduced.

## Slide 15: New Approach: Always efficient
Add obstacles to have a maximum ratio of between 3 and 6.
Flocculation efficiency can be considered constant (and close to 1)
Our design equations don’t need an efficiency term
30 L/s
10 L/s
Notes: This range of H/S is necessary to ensure that there is always a solution when switching from two expansions per baffle to one expansion per baffle.

## Slide 16: Viscous collisions or inertial collisions
Prior to 2016 I had assumed that the appropriate length scale comparison was particle separation distance and Kolmogorov length scale – thus concluded inertia was important
Particle separation distances are smaller than inner viscous length scale
Collisions in turbulent flocculators are dominated by viscosity (fluid shear, not turbulent eddies)*
2016
* Edge of knowledge

## Slide 17: Ten State Standards
The detention time for floc formation should be at least 30 minutes with consideration to using tapered (i.e., diminishing velocity gradient) flocculation. The flow‑through velocity should be not less than 0.5 nor greater than 1.5 feet per minute.
Agitators shall be driven by variable speed drives with the peripheral speed of paddles ranging from 0.5 to 3.0 feet per second. External, non-submerged motors are preferred.
Flocculation and sedimentation basins shall be as close together as possible. The velocity of flocculated water through pipes or conduits to settling basins shall be not less than 0.5 nor greater than 1.5 feet per second. Allowances must be made to minimize turbulence at bends and changes in direction.
Baffling may be used to provide for flocculation in small plants only after consultation with the reviewing authority. The design should be such that the velocities and flows noted above will be maintained.
http://10statesstandards.com/waterrev2012.pdf
Hydraulic flocculators allowed only by special permission!
Notes: What does a hydraulic flocculator look like?
What do you need to know in order to design a flocculator?
How might we decide what the spacing should be between baffles?

## Slide 18: Collision Potential
The target collision potential used for the design of AguaClara plants since about 2013 has been 37,000
The actual collision potential in operating AguaClara plants may be lower because the head loss per baffle may be lower than we assumed

## Slide 19: Energy use (head loss) in flocculation controls velocity gradient
Head loss
  High head loss results in a taller building for the water treatment plant
  High head loss means higher velocities and that reduces settling of flocs in the flocculator
  Some gravity flow water supplies don’t have much elevation difference between source and storage tank
Velocity gradient (G)
  Higher allows lower residence time
  Higher results in smaller flocs

## Slide 20: The Influence of or GMax
The value of or determines the head loss through the flocculator
Maximum size of the flocs is controlled by
  or (assuming shear limits attachment)
  GMax or eMax (assuming floc break up controls max size)
eMax = 10 mW/kg (GMax = 100 Hz) was the AguaClara standard (2011-2015)
Summer 2015 new designs have head loss of approximately 40 cm
  Expect smaller flocs (but still captured by plate settlers)
  Less sedimentation of flocs in flocculator
  Smaller flocculator
Casey Garland has tested values as high as 340 Hz
Not yet known
Notes: Likely much harder to attach than to stay together once connected.
Flocs grow in low shear zones
Flocs breakup in high shear zones
Likely that initial attachment phase is more difficult than staying together once attached. Thus breakup likely doesn’t happen much in a uniform shear environment.

## Slide 21: The design inputs for flocculation
We need collisions and thus Gq is a logical design specification
We need to specify energy use
  Velocity gradient -
  Energy dissipation rate -
  Total head loss -
Or t (q)
More time helps diffusion of coagulant nanoparticles to clay surfaces
Higher G means smaller flocs and more elevation drop (head loss) through flocculator
Current approach
Notes: This is in part because we don’t have a rational basis to choose the G value for flocculation. There is an economic impact of increasing head loss, so we use that constraint for now.

## Slide 22: Key equations that we can use to design flocculators
Minor loss equation
Energy dissipation rate must match the rate that mechanical energy is lost*
Fluid strain is set by the energy dissipation rate and viscosity
*On average, potential energy lost in a flow expansion is dissipated in the residence time of that flow expansion
Continuity, mass conservation
Solve to get G as a function of flow rate and geometry

## Slide 23: Our current choice of parameter that sets energy input is head loss
Head loss is independent of temperature
Velocity gradient is f(temperature)
Start with (, q) and coldest temperature
  Calculate q
  Calculate hFloc
Start with (hFloc, q) and coldest temperature
  Calculate
  Calculate q
(and hence q) will increase when the flocculator is operated at warmer temperatures due to decrease in viscosity
Current approach
Option 2
Option 1

## Slide 24: Design the reactor geometry to get the target velocity gradient
W
S
A
Kinetic energy dissipated per residence time
Continuity
is height of one expansion zone. Could be the depth of water if the only expansion is from the 180 degree bend
This is our general equation relating velocity gradient to reactor geometry
Rectangular geometry
Notes: What are the 3 related parameters that set how much energy the flocculator uses?
Gt
Which parameter sets the spacing between baffles? (G, EDR, hl)
Which parameter sets the flocculator volume? t

## Slide 25: Solve for channel width to set constraints on viable solutions
This is the minimum channel width if we set = 3 and set the expansion height to equal water depth
As channel gets narrower the spacing between baffles gets larger.
Channels narrower than this would have barely any or negative baffle overlap!
Elevation view
Notes: What happens if I make the channel narrower and narrower? What fails?
Find the range of W
Set W
Find the range of He
Set He
Find S

## Slide 26: Meet the target H/S by decreasing the distance H between obstacles
This design was first used at the plant in San Juan Guarita en western Honduras
Notes: [PLACEHOLDER TEXT]

## Slide 27: Minimum number of expansions per depth of flocculator (given W)
Solve for maximum distance between expansions, , using = 6
Round up to get the minimum number of expansions per depth of the flocculator
Eliminate S
Water depth at the end of the flocculator
Distance between flow expansions

## Slide 28: Our Design Approach Given energy ( or ) and Gq
Start big and then design the details
  Calculate volume of flocculator
  Split it into channels
  Then design baffles, and obstacles to fill the channels to get target
We can use this design approach because we are assuming that we will design for high efficiency (3< <6) and thus we don’t have to add extra volume to account for inefficiencies. (Don’t forget this requirement!)
(AguaClara approach as of summer 2015)

## Slide 29: Design Algorithm (as of 2016) Start with and Gq
Velocity gradient and flocculator volume given head loss and collision potential
Minimum channel width required to achieve >3 and required for constructability
Number of channels by taking the total width and dividing by the minimum channel width (floor)
Channel width (total width over number of channels)
Maximum distance between expansions
Minimum number of expansions per baffle space
Actual distance between expansions
Baffle spacing
Calculate the obstacle width to obtain the same jet expansion conditions as produced by the 180 degree bend

## Slide 30: Viscous Collision Potential per Flow Expansion (the detailed perspective)
Collision potential for one flow expansion
Energy dissipation rate is energy loss per time
Collision potential is a function of velocity. This suggests that a flocculator would perform poorly if the flow rate was decreased. I don’t know if anyone has ever demonstrated that!
Hydraulic residence time for one expansion zone
These are the average velocities through the expanded flow area
Height of one expansion zone (in a vertical flow flocculator)

## Slide 31: Almost Real Designs (Flocculator exit depth of 2 m)
What sets maximum channel width?
What sets minimum channel width?
Why this cycle of channel widths?
Human hip
Sheet width
Number of channels
1
2
3
4
5
Here we allowed odd number of channels
Notes: Max is sheet width
Min is half sheet (hip width) or the width required to not get an H/S less than 3.
Cycle is due to increasing number of channels (integers)

## Slide 32: Velocity guidelines?
Why does V increase with flow rate?
Why does V increase in steps?
Why does V remain constant above 70 L/s?
Notes: Velocity is lower for low flow rates the distance between expansions is lower.
Velocity increases in steps because there is an integer number of expansions per depth of flocculator.
Above 70 L/s there are no additional obstacles and the flocculator channel is just getting wider.

## Slide 33: Design Scaling (Design Engine version 7099)
50 L/s
0.56 m wide channels
6.68 m long
10 L/s
0.53 m wide channels
4.33 m long
70 L/s
0.72 m wide channels
7.27 m long
20 L/s
0.55 m wide channels
5.90 m long
Notes: Extra obstacles for 10 and 20 L/s.
Channels get wider

## Slide 34: More details
The ports between channels should have the same cross sectional area as WS
The number of chambers per canal (except in the last canal) is even – the number of baffles is odd
The number of chambers in the last canal is odd – the number of baffles is even
Why?

## Slide 35: Use a Pipe with orifices to make a flocculator for small flows (S=D)
Continuity
Here we use Ke from typical baffled flocculators and H/S of 6 to minimize number of chips required. Round up to nearest inner pipe diameter? Or round down to get higher velocities to prevent sedimentation?
DPipe
hL
DOrifice
Here we assume that S is like D
extra

## Slide 36: Estimate the orifice diameter
The head loss for these orifices spaced so closely may be less than what we calculate
  Vena contracta may not be as severe for orifices that are close to the inner diameter of the pipe
  Insufficient length for full expansion before next orifice
We need to estimate Ke!
extra

## Slide 37: Estimate the orifice diameter using the required value of Ke given the actual pipe ID
Need to find actual Ke given actual pipe diameter to develop target G. The actual Ke will increase to get the same head loss given the slower velocity in the larger diameter pipe.
Replace residence time with volume/Q
extra
https://neutrium.net/fluid_flow/pressure-loss-from-fittings-expansion-and-reduction-in-pipe-size/

## Slide 38: Use a Pipe with orifices to make a flocculator for small flows (H=D)
Continuity
Round to nearest inner pipe diameter? Or round down to get higher velocities to prevent sedimentation?
DPipe
hL
DOrifice
Here we assume that H is like D
extra

## Slide 39: An interesting design No this wasn’t AguaClara…
Notes: How could you fix this?

## Slide 40: CEPIS Horizontal Flow Flocculator
Notes: Horizontal flow results in shallower flocculators for low flow rate plants. Thus vertical flocculators take up less area and thus vertical flocculators are less expensive. Also head loss has less of an impact on flow area in vertical flocculator.

## Slide 41: Reflection Questions
How does the collision potential in a flocculator change with flow rate?
What is the ratio of to for well designed hydraulic flocculators (extra info!)?
Why might mechanical flocculators break more flocs than hydraulic flocculators?
Notes: If we decrease flow, then Gtheta decreases!!!!
For small H/S need to take the average energy dissipation rate and multiply by 2 to get the max.

## Slide 42: Reflection Questions
What are some alternate geometries?
How else could you generate head loss to create collisions?
0.6S
0.4S
Notes: So easy! Add obstructions! Cylinders, plates, etc.

## Slide 43: Reflection Questions
What is the relationship between potential energy loss and the average velocity gradient in a flocculator?
How did AguaClara get around the 45 cm limitation?
How does the non uniformity of e (or G) influence efficiency of energy use?

## Slide 44: Conclusions
Energy dissipation rate determines the spacing of the baffles.
Energy is used most efficiently to create collisions when the energy dissipation rate is uniform. Therefore H/S between 3 and 6 is best.
Collision potential is a function of geometry and a function of flow rate

## Slide 45: Shear limits the size of flocs by not allowing them to grow
Tangent velocities of the approaching particle surfaces increase as size of either particle increases
Bonds formed on impact are unzipped due to rotation and high tangent velocities (perhaps a maximum relative velocity?)
extra

## Slide 46: Shear limits the size of flocs by tearing them apart
A floc in turbulent flow experiences a shear force due to the drag of the fluid on the floc caused by the velocity gradient
The floc will also rotate and this will reduce the difference in velocity between the floc and the fluid
*edge of knowledge – in well designed flocculators floc breakup is likely not significant and floc growth is the limiting factor.
extra
Notes: 46
The number of bonds per unit area in the central plane of the floc decreases as the floc grows larger.

## Slide 47: The Energy Dissipation Rate isn’t uniform
Ideally (for optimal efficiency) the flocculator would have a completely uniform energy dissipation rate
We can evaluate the energy dissipation rate uniformity of various designs as a function of H/S
extra

## Slide 48: Estimating the ratio
Definition of
True for large where the jet fully expands before the next turn
Energy lost
time
Control volume analysis
extra
Notes: THE INFLUENCE OF VISCOSITY ON MIXING IN JET REACTORS
Jo BALDYGA, J. R. BOURNE* and R. V. GHOLAP
Chemical Engineering Science, Vol. 50, No. 12, pp. 1877-1880, 1995
It is expected that P.Jet is a function of the jet geometry.

## Slide 49: Estimating
The transition value for H/S is at 5 (from CFD analysis) (this is our weakest assumption)
has a value of 2 for <5 (CFD analysis and Haarhoff, 2001)
has a value of for > 5
Solve for when = 5
extra
Notes: “Overlap ratios of less than 5 result in normalized G-values of less than 1.5.” Towards optimal design parameters for around-the-end hydraulic flocculators, Johannes Haarhoff and Jeremia J. van der Walt.
Journal of Water Supply: Research and Technology—AQUA | 50.3 | 2001
We can move from a G ratio to a EDR ratio by squaring the G ratio.

## Slide 50: Results of the CFD analysis and our model equations
e is more uniform when H/S is between 3 and 6.
For <5
Prior to 2015 all AguaClara designs had an H/S >5.
Future designs will have 3<<6
extra
Notes: These results require a Pi.PlaneJet value of 0.225.