## Slide 1: Flow Control and Measurement
Creativity without a trip
Variations on a drip
Giving head loss the slip
Chemical doses that don’t dip
Here’s a tip!
We can use smart fluids to eliminate software, computers, and electronics!

## Slide 2: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 3: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 4: Fluids Review
What causes drag?
Best orientation to reduce drag?

## Slide 5: Streamlines
Draw the streamlines that begin on the upstream side of the object for these two cases
Which object has the larger wake?
Which object has the lower pressure in the wake? (if streamlines are bending hard at the point of separation, then the streamlines will be close together…)

## Slide 6: Why is there drag?
Fluid separates from solid body and forms a recirculation zone
Pressure in the recirculation zone must be low because velocity in the adjacent flowing fluid at the point of separation is high
Pressure in recirculation zone (the wake) is relatively constant because velocities in recirculation zone are low
Pressure behind object is low - DRAG

## Slide 7: Fluids Review
Where should the luggage go?
Which equation for head loss?
Which process is inefficient?
Pipeline design

## Slide 8: Orifice Equation
Bernoulli equation (no energy loss)
Area of the constricted flow
Continuity equation
Orifice Equation (memorize this!)
This equation applies to a horizontal orifice (so that the depth of submergence is constant). For depth of submergence larger than the diameter of the orifice this equation can be applied to vertical orifices. There is a general equation for vertical orifices in aide.physchem.
z1
z2 = 0
mechanical
^
Flow contraction!

## Slide 9: Two kinds of drag Two kinds of head loss
Drag (external flows)
Skin (or shear) friction
  Shear on solid surface
  Classic example is flat plate
Form (or pressure) drag
  Separation of streamlines from solid surface and wake results in a…
  Flow expansion (behind object)
Head loss (internal flows)
Major losses (hf – friction)
  Shear on solid surface
  Shear on pipe walls
Minor losses (he – expansion)
  Separation of streamlines from solid surface results in a…
  Flow expansion
Energy equation (NOT THE BERNOULLI EQUATION)

## Slide 10: Head Loss in a Long STRAIGHT Tube (due to wall shear): Major Losses
Darcy Weisbach:
Transition from turbulent to laminar occurs at Re~2100
Applies for BOTH laminar and turbulent flow,
but what is the friction factor for wall shear, f? First, find Reynold’s number

## Slide 11: Head Loss in a Long STRAIGHT Tube (due to wall shear): Major Losses
Laminar
if Re < 2100,
Major loss equation simplification (for
laminar flow only!):
Hagen-Poiseuille
Flow proportional to hf
Swamee-Jain
Turbulent
if Re > 2100,
Where Ɛ is the wall roughness
(no equation simplification)

## Slide 12: Frictional Losses in Straight Pipes
0.01
0.1
1E+03
1E+04
1E+05
1E+06
1E+07
1E+08
Re
friction factor
laminar
0.04
0.03
0.02
0.015
0.01
0.008
0.006
0.004
0.002
0.001
0.0008
0.0004
0.0002
0.0001
0.00005
smooth
0.05

## Slide 13: Head Loss: Minor Losses
Head (or energy) loss (hL) due to: outlets, inlets, bends, elbows, valves, pipe size changes
Losses are due to expansions
Losses can be minimized by gradual expansions
Minor Losses have the form where Ke is the loss coefficient and V is some characteristic velocity (could be contracted flow or expanded flow)
When V, KE  thermal

## Slide 14: Head Loss due to Sudden Expansion: Conservation of Energy
zin = zout
Relate Vin and Vout?
in
out
Relate pin and pout?
Mass
Momentum
Where is p measured?___________________________
At centroid of control surface
z
x
Notes: Suppose mechanical energy is conserved (it isn’t!) in this flow. What would have to be true of the downstream pressure? (It would have to be higher than the upstream pressure.)
Does water like to move from a region of low pressure into a region of high pressure?
Flow into region of higher pressure causes any curved streamlines to curve even more! Given that the flow is slowing down the streamlines MUST BE diverging. The increasing pressure causes the streamlines to bend even more. We get turbulence!

## Slide 15: Head Loss due to Sudden Expansion: Conservation of Momentum
Apply in direction of flow
Neglect surface shear
Pressure is applied over all of section 1.
Momentum is transferred over area corresponding to upstream pipe diameter.
Vin is velocity upstream.
1
2
Ain
Aout
x

## Slide 16: Head Loss due to Sudden Expansion
Discharge into a reservoir?__________________
Energy
Momentum
Mass
Loss coefficient = 1
2
2
2
Ke
Ke’
Notes: Emphasize the minor loss coefficient is defined based on some relevant velocity. We can chose either V1 or V2. But the magnitude of the minor loss coefficient is determined by which velocity we use. We need to choose one and be consistent. The velocity that we choose will be a function of convenience. Minor losses are proportional to the square of the velocity. This is true whether the flow is turbulent or laminar!

## Slide 17: Minor Loss Coefficient for an Orifice in a Pipe (DOrifice < < Dpipe)
DPipe
hL
DOrifice
Minor loss coefficient
Expansion losses
This is Vout, not Vin
e for expansion
Vena contracta area
extra
Notes: Draw the orifice case in detail showing expansion zone

## Slide 18: Minor Loss Coefficient for an Orifice in a pipe
extra
The expansion starts from the vena contracta
Notes: Draw the orifice case in detail showing expansion zone

## Slide 19: Equation for the diameter of an orifice in a pipe given a head loss
Minor losses dominate, thus he = hL
extra
Where do changes in pressure occur?
Where does head loss occur?

## Slide 20: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 21: Applications of Constant Flow
POU treatment devices (Point of Use)
  clay pot filters
  SSF (slow sand filters)
  Arsenic and fluoride removal devices
Reagent addition for community treatment processes
  Alum or Poly Aluminum Chloride (PACl) ____________
  Calcium or sodium hypochlorite for ____________
  Sodium carbonate for _____________
A flow control device that maintains a constant dose as the main flow varies
coagulation
disinfection
pH control

## Slide 22: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 23: If you had electricity…
Metering pumps (positive displacement)
  Pistons
  Gears
  Peristaltic
  Diaphragm
Valves with feedback from flow sensors
So an alternative would be to raise the per capita income and provide RELIABLE electrical service to everyone…
But a simpler solution with fewer moving parts would be better!

## Slide 24: A couple of observations…
Municipal water treatment often fails due to unreliable chemical dosing of chlorine and coagulants
Failure modes include
  Inability to easily set the target dose
  Lack of easy method for operators to monitor flow
  Poor designs that don’t maintain a constant dose

## Slide 26: Dosing at a large city Water Treatment Plant in Nepal
One 25 kg block of alum at a time
Placed in the channel carrying raw water into the plant

## Slide 27: Salt water electrolytic chorine generators

## Slide 28: Chlorine tablet chlorinators

## Slide 29: The Challenge of Chemical Metering (Hypochlorinator)
What is the simplest representation that captures the fluid mechanics of this system?
Raw water entering distribution tank
Overflow tube
PVC valve
PVC pipe
Access door to distribution tank
Chlorine drip
Chlorine solution
Access door to hypochlorinator tank

## Slide 30: Hole in a bucket doesn’t give a constant flow rate
Vena contracta
Orifice
This is NOT a minor loss coefficient
It is the ratio of the vena contracta area to the orifice area
Q is flow rate [volume/time]

## Slide 31: Use Conservation of Mass and Minor Loss equation [Two unknowns (Q, h)]
Our goal: To determine the height (h) of chlorine in the tank and its flow rate out of the tank (Q) as a function of time (t)
h0

## Slide 32: Use Conservation of Mass and Minor Loss equation [Two unknowns (Q, h)]
h0
Orifice in the PVC valve
Integrate to get h as f(t)
volume
Plan view area
Mass conservation on liquid in tank
Minor loss equation

## Slide 33: Finding the chlorine depth as f(t)
Integrate
Solve for height
Separate variables

## Slide 34: Finding Q as f(t)
Find AValve as function of initial target flow rate
Set the valve to get desired dose initially
Finding Q as f(t)

## Slide 35: Surprise… Q and chlorine dose decrease linearly with time!
Relationship between Q0 and ATank?
Assume flow at Q0 for time (tDesign) would empty reservoir
Linear decrease in flow with time
Notes: When does the flow rate go to zero?
What is the average flow rate during this process if the tank is drained completely? 0.5 Q0.
How could you modify the design to keep Q more constant?

## Slide 36: Reflections
Let the discharge to atmosphere be located at the elevation of the bottom of the tank…
When does the flow rate go to zero?
What is the average flow rate during this process if the tank is drained completely?
How could you modify the design to keep Q more constant?

## Slide 37: Effect of tank height above valve
Case 1, h0=50 m, htank = 1 m, tdesign=4 days
Case 2, h0=1 m, htank = 1 m, tdesign=4 days
htank

## Slide 38: A related tangent… Design a drain system for a tank
Substitute valve diameter
Here Ke is the total minor loss for the drain system
0
Integrated results giving h as f(t)
Empty the tank completely

## Slide 39: Brainstorm: Constant Flow
Why did the previous systems not provide constant flow of chlorine?
Why is this hard?
What are the desired properties of the device that meters chemicals into a water treatment plant?
Notes: What is the simple energy source?
Big question is can we develop a dosing system based on fluid dynamics.
Elegant simplicity
Few moving parts
Easy for the operator to set the chemical dose (rather than flow)

## Slide 40: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 41: Constant Head: Floats
orifice
VERY Flexible hose
Head can be varied by changing buoyancy of float
Supercritical open channel flow!
Unaffected by downstream conditions!

## Slide 42: Hypochlorinator with float design
What is the simplest representation that captures the fluid mechanics of this system?
Raw water entering distribution tank
Overflow tube
PVC valve
PVC pipe
Access door to distribution tank
Chlorine drip
Float
Transparent flexible tube
Orifice
Chlorine solution
Access door to hypochlorinator tank

## Slide 43: Floating Bowl
Adjust the flow by changing the rocks
Need to make adjustments (INSIDE) the chemical tank
Rocks are submerged in the chemical
Safety issues

## Slide 44: Constant Head: Overflow Tanks
Surface tension effects here
What controls the flow?

## Slide 45: Constant Head: Marriot bottle
A simple constant head device
Why is pressure at the top of the filter independent of water level in the Marriot bottle?
What is the head loss for this filter?
Disadvantage? ___________
batch system

## Slide 46: Constant Head: Float Valve
Float adjusts opening to maintain relatively constant water level in lower tank (independent of upper tank level)
NOT Flow Control!
?
Force balance on float valve?
dorifice
dfloat
hsubmerged
htank

## Slide 47: Our goal is to adjust the flowrate and then maintain constant flow
Head (or available energy to push fluid through the flow resistance) (voltage drop)
Flow resistance (resistor)
  ____________________________________
  ____________________________________
  ____________________________________
Vary either the head or the flow resistance to vary the flow rate (current)
  Vary head by adjusting the constant head tank elevation or the outlet elevation of a flexible tube
  Vary orifice size by adjusting a valve
Orifice i.e. small hole or restriction
Long straight small diameter tube
Porous media

## Slide 48: Variable Orifice
Variable head or variable resistance?
How is flow varied?
Variable orifice area
How would you figure out the required size of the orifice?
Notes: Dan Smith
Steve
Constant head, vary resistance!

## Slide 49: Float valve and small tube variable head
Flow control device
Small diameter tubing
hL
chemical stock tank
If laminar flow!
Neglecting minor losses
straight
^
Notes: Peter von Bucher
Presidential Prez: Alana Jonat
Executive Mastermind: Roslyn Odum

## Slide 50: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 51: Hypochorinator Fix
http://web.mit.edu/d-lab/honduras.htm
What is good?
How could you
improve this system?
What might fail?
Safety hazards?
Notes: http://web.mit.edu/d-lab/honduras.htm

## Slide 52: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 53: AguaClara Technologies
“Almost linear” Flow Controller
Linear Flow Orifice Meter
Linear Chemical Dose Controller

## Slide 54: AguaClara approach to flow control
Controlled variable head
  Float valve creates constant elevation of fluid at inlet to flow control system
  Vary head loss by varying elevation of the end of a flexible tube
Head loss element
  Long straight small diameter tube
  We didn’t realize the necessity of keeping the tube straight until 2012 and thus our early flow controllers had curved dosing tubes
extra

## Slide 55: Early Flow Controllers
Nonlinear relationship between flow and height of end of tube

## Slide 56
Holes to choose the alum dose
Rapid Mix
The fluid level in the bottle should be at the same level as the 0 cm mark
Tube from the stock tank
Air vent
Raw water
Flexible tube with length set to deliver target maximum flow at maximum head loss
Float valve
1 L bottle
In our first flow controllers we didn’t realize how important “straight” was! We ignored minor losses and minor losses weren’t minor!
Hagen–Poiseuille

## Slide 57: Requirements for a Flow Controller
Easy to Maintain
Easy to change the flow in using a method that does not require trial and error
Needs something to control the level of the liquid (to get a constant pressure)
Needs something to convert that constant liquid level into a constant flow
extra
Notes: Constant head
Variable head loss
Tube as resistance element and also used to vary the head loss

## Slide 58: Hypochlorinator Fix
Raw water entering distribution tank
Overflow tube
Access door to distribution tank
Chlorine solution
Access door to hypochlorinator tank
extra

## Slide 59: Installing a Flow Controller for dosing Chlorine
extra

## Slide 60: Dose Controller: The QC Control Problem
How could we design a device that would maintain the chemical dose (C) as the flow (Q) through the plant varies?
Somehow connect a flow measurement device to a flow controller (lever!)
Flow controller has a (mostly) linear response
Need height in entrance tank to vary linearly with the plant flow rate – solution is The Linear Flow Orifice Meter (LFOM)
Dose is the chemical concentration in the water

## Slide 61: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 62: Linear Flow Orifice Meter
Sutro Weir is difficult to machine
Mimic the Sutro weir using a pattern of holes that are easily machined
Install on a section of PVC pipe in the entrance tank
Used at all AguaClara Plants except the first plant (Ojojona)
Invented by AguaClara team member David Railsback, 2007

## Slide 63: Linear Orifice Meter
Photo by Lindsay France

## Slide 64: Linear Flow Orifice Meter
Holes must be drilled with a bit that leaves a clean hole with a sharp entrance (hole saws are not a good choice) (Don’t deburr the hole!)
The sharp entrance into the hole is critical because that defines the point of flow separation for the vena contracta
The zero point for the LFOM is the bottom of the bottom row of orifices
extra

## Slide 65
Raw water
Max water level in floc tank
Bottom of entrance tank
Min water level in entrance tank
Max water level in entrance tank
Wall height of entrance tank
5 cm
5 cm
20 cm
? cm
Linear Flow Orifice Meter
Flow Controller
What must the operator do if the plant flow rate decreases?
extra

## Slide 66: Overview
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 67: Linear Dose Controller
Combine the linear flow controller and the linear flow orifice meter to create a Linear Dose Controller
Flow of chemical proportional to flow of plant (chemical turns off when plant turns off)
Directly adjustable chemical dose
Can be applied to all chemical feeds (coagulant and chlorine)
Note: This is NOT an automated dose device because the operator still has to set the dose

## Slide 68
H
Open channel supercritical flow
Drop tube
Dosing tubes
Stock Tank of coagulant
Lever
LFOM
Float
Constant head tank
Float valve
Slider
Purge valves
Notes: This is a basic schematic of what research and design teams have come up with after many years of work. The stock tank holds a stock chemical solution which is connected to a constant head tank. The constant head tank is regulated by a float valve which keeps the chemical depth constant. A large diameter tube leads from the stock tank to one or more small diameter long straight dosing tubes. A large diameter flexible leads to a drop tube with “open channel super critical flow”, where the chemical flows to be added to the plant’s influent water. The drop tube is connected to a lever via a slider. The plant operator sets the slider at the desired coagulant dose based upon characteristics of the influent water. The float attached to the lever changes position as flow rate into the plant changes, thus changing the elevation of the large diameter tube’s outlet, and maintaining a constant chemical dose.

## Slide 69
H
Decrease dose

## Slide 70
Increase dose
H

## Slide 71
H
Half flow

## Slide 72
Plant off

## Slide 75
Lever
Constant Head Tanks
Linear Flow Orifice Meter
Dosing Tubes

## Slide 77
Atima doser: Three 1/8” diameter tubes, 1.93 m long, 187.5 g/L stock solution of PACl, 5 to 48 mg/L dose range.
Lever
Constant Head Tank
Coagulant Stock Tank
Linear Flow Orifice Meter
Dosing Tubes
Flow calibration column
Notes: Dosificador: 3 mangueras de 1/8" diámetro interno, 1.93m longitud, concentración madre de 187.5 g/L de PAC, dosis máxima 48 mg/L, dosis mínima 5 mg/L.

## Slide 78: Chemical Dose Controller
The operator sets the dose directly
No need for calculations
Visual confirmation
A key technology for high performing plants
More improvements are possible!
30 25 20 15 10

## Slide 79: Stock tanks, calibration columns, constant head tanks, dosing tubes, lever and slider, LFOM

## Slide 80: What’s wrong with this drawing? Find the missing piece

## Slide 81: Our goal is to design a more modular dosing system

## Slide 82: Identify everything!

## Slide 83: Design specifications for the float valve
The float valve has an orifice that restricts the flow of the chemical and that dominates the head loss between stock tank and constant head tank. Different float valves have different sizes of orifices.
Chemical Feed Tank
Why are we concerned with the orifice head loss?
Where else is there head loss?
Is this a minimum or a maximum orifice diameter?
Why not increase Dh?
Notes: We must also design the tubing diameter that delivers the chemical to the constant head tank
If the orifice head loss is too large the float valve will end up controlling the flow rate when the stock tank begins to empty.
This is the minimum orifice diameter. Larger would be okay.
We could increase deltah, but that raises the stock tank and the plant operator has to fill this stock tank and climb stairs to get to it.

## Slide 84: Constraints on flow controller Dosing tube design
Flow must be laminar (Re<2100)
Minor losses must be small (small V!)
  It took us a while to discover how critical this constraint is!
Dosing tube must “be reasonable” length which might mean shorter than an available wall in the plant.
Designing dose controllers over a wide range of chemical flow rates requires good engineering
How can I get a shorter tube?
Notes: Get a shorter tube by using a smaller diameter tube. May need to use multiple smaller diameter tubes.

## Slide 85: Nonlinearity Error Analysis: The problem caused by minor losses
Actual head loss
Linearized model of head loss
Calibrate at max flow
y = m x
How can we make minor losses small?
Notes: Red is hypothetical (what would happen if there weren’t any minor losses)
Blue is what really happens with minor losses
Green is how we calibrate our doser and thus the gap between blue and green represents the error. The error as a percentage of the target is largest as flow approaches zero.
FCM design 10.xmcd

## Slide 86: Relationship between Q and L given minor loss error constraint
Relationship between minimum tube length and maximum flow from the error constraint (both unknowns – we need another equation between Q and L!)
Plug in head loss equations. Take the limit as Q→0.
Solve for L
Set a limit on the error caused by nonlinearity (we use 0.1)
Notes: If L is longer than this, then the flow rate will decrease and minor losses will decrease. Thus this is the shortest tube that can possibly work as a function of flow rate. This assumes a continuously variable D such that the velocity is always at the maximum allowed velocity given the error constraint.

## Slide 87: Relationship between Q and L given head loss constraint
2nd equation relating Q and L is total head loss
Combine two equations
Solve for Max Q
1st equation relating Q and L – error constraint
This is the minimum D that we can use assuming we use the shortest tube possible that meets the error constraint.
Notes: The head loss constraint is based on what elevation difference we want to have between the constant head tank and the end of the dosing tube.
If we decrease the error, then we need to use a larger D in order to get a lower V.

## Slide 88: Dosing Tube Lengths
This is the shortest tube that meets the minor loss constraint.
This is for laminar flow!
major
minor
If the tube isn’t operating at its maximum flow (for error constraint) then use this equation.
Does tube length increase or decrease if you decrease the flow while holding head loss constant?
The equations below give tube length to achieve any target flow

## Slide 89: Tube Diameter for Flow/Dose Controller (English tube sizes)
Reynolds
Continuity
Minor Loss Errors
Viscosity = 1.0 mm2/s, ΣKe = 2
2100
Is this a min or max D?
Notes: FCM design 9.xmcd
The Reynolds constraint gives a minimum diameter!

## Slide 90: Dose Controller Accuracy
Float valves only attenuate the fluctuations in level of the fluid surface
Surface tension effects at the location where the fluid switches from closed conduit to open channel flow (the end of the dosing tube) could cause errors of a few millimeters
The weight of the tubing and slide supported by the lever will apply different amounts of torque to the lever depending on the dose chosen. This determines the required diameter of the float
H

## Slide 91: Maximum Plant Flow Rate Using Linear Flow Controller
Assume the PACl concentration is 160 g/L, the maximum PACl dose is 30 mg/L, and the maximum flow in a 5 mm diameter dosing tube is about 8.7 mL/s.
Mass conservation
P = Plant
C = Chemical Feed
What is the solution for larger plants? ___________
Multiple tubes

## Slide 92: Dose Control Summary
Laminar tube flow and linear flow orifice meters
  Coagulant dosing for plants with flow rates less than about 200 L/s
  Chlorine dose controllers even for larger plants
These devices are robust AND a good design requires excellent attention to details
  No small parts to lose
  No leaks
  Compatible with harsh chemicals
  Locally sourced materials if possible
  Dosing tubes must be straight
  Must account for viscosity of the chemical
  Minor losses must be minor!

## Slide 93: Extras!
Fluids Review
Applications of flow control
If you had electricity
Constant head devices
  Overflow tanks
  Marriot bottle
  Float valve
  Floating bowl
Hypochlorinators in Honduras
AguaClara Flow Controller
Linear Flow Orifice Meter
AguaClara Linear Dose Controller
Extra
  Orifices and surface tension
  Viscosity

## Slide 94: Extending the range of the flow controllers
A single laminar flow controller will not be able to deliver sufficient alum for a large plant
Could you design a turbulent-flow flow controller?
Could we go non linear with both flow measurement and flow control to get a simple design for larger water treatment plants?
Clogging will be less of an issue with larger flows
What are our options for relationships between flow rate and head loss?
extra
Notes: Easy option is to use multiple LFOMs in parallel, but that is difficult for
Learn from the Sutro weir Use a Sutro weir or LFOM design for the flow controller.

## Slide 95: Closed Conduit Flow options for Flow Controllers
Laminar flow in a tube
Turbulent flow in a tube
Orifice flow
Valid for both laminar and turbulent flow!
Governing equation
Range Limitations
Low flow rates
High flow rates to achieve constant f
extra

## Slide 96: Open Channel Flow Relationships
Sharp-Crested Weir
V-Notch Weir
Broad-Crested Weir
Sluice Gate (orifice)
Explain the exponents of H!
extra
Notes: Sharp crested weir www.fao.org/docrep/T0231E/t0231e4g.gif
Broad crested weir http://mrgcd.com/cms/kunde/rts/mrgcdcom/Docs/712740416-10-12-2007-11-33-00_files/image006.jpg

## Slide 97: Dose Controller with nonlinear scale
General Flow – Head Loss relationships for chemical feed and plant flow
Concentration of the chemical in the plant
Connect the two heads with a lever, therefore the two heads must be proportional
Is the plant concentration constant as the plant flow rate changes?
extra

## Slide 98: Constant dose with changing plant flow requirement
What must be true for Cp to be constant as head loss, hp changes?
What does this mean?
What are our options?
extra

## Slide 99: Dose scale on the lever arm?
KL is the ratio of the height change of the float to the height change of the flow controller
8
10
12
14
16
18
20
Pivot Point
Alum dose (mg/L)
This relationship makes it difficult to accurate control a wide range of alum dosages on a reasonable length lever
extra

## Slide 100: AguaClara Dose Control History
Laminar tube flow and simple orifice
Laminar tube flow and linear flow orifice meter
Dose controller that combines laminar tube flow and linear flow orifice meter
Dose controller with orifice flow for both flow control and measurement
Dose controller with variable valve and simple orifice
control
measurement
extra

## Slide 101: Variable dosing valve: For coagulant dosing for plant flows above 100 L/s
Photo courtesy of Georg Fischer
Piping Systems
This method has not yet been attempted. The dose will be set by turning the valve. The valve will replace the head loss tube. The transition to open channel flow will be on a lever that tracks plant flow rate but no slider will be required. The exit from the entrance tank will be a simple orifice system. The system will still respond to plant flow changes correctly.
extra
Notes: Monica Hill’s research https://confluence.cornell.edu/display/AGUACLARA/High+Flow+Dose+Controller

## Slide 102: Surface Tension
Is the force of gravity stronger than surface tension?
2prs
Fs=
Fp=
Will the droplet drop?
extra

## Slide 103: Surface Tension can prevent flow!
0.050
0.055
0.060
0.065
0.070
0.075
0.080
0
20
40
60
80
100
Temperature (°C)
Surface tension (N/m)
Solve for height of water required to form droplet
extra

## Slide 104: A constraint for flow control devices: Surface Tension
Delineates the boundary between stable and unstable
Flow control devices need to be designed to operate to the right of the red line!
droplets form to right of line
extra

## Slide 105: Kinematic Viscosity of Water
0.0E+00
5.0E-07
1.0E-06
1.5E-06
2.0E-06
0
20
40
60
80
100
Temperature (C)
Kinematic Viscosity (m
2
/s)
This is another good reason to have a building around AguaClara facilities!
extra

## Slide 106: Kinematic Viscosity of Coagulants
extra
Notes: Matthew J. Higgins Master of Engineering 2011
Karen Swetland
Interesting property that viscosity increase is almost directly proportional to concentration at 250 gm/L.

## Slide 107
Sand column
HJR
Holding container (bucket or glass column)
Pong pipe
Sealing pipe
Driving head for sand column
Upflow prevents trapped air
(keyword: “prevent”)!
What is the purpose of the sand column?
Porous media as resistance element
extra
Notes: Heather Nelson
Jeannette Harduby
Rudi Schuech
Constant resistance, vary head

## Slide 108: Porous Media Head Loss: Kozeny equation
Velocity of fluid above the porous media
Analogy to laminar flow in a pipe
k = Kozeny constant
Approximately 5 for most filtration conditions
Dynamic viscosity
Kinematic viscosity
extra
Notes: Adapted from equation 8.2 in 5th edition of Water Quality and Treatment: A Handbook of Community Water Supplies by AWWA 1999.

## Slide 109: Orifice Image
extra

## Slide 110: Tube Diameter for Flow/Dose Controller (English tube sizes)
Increasing the viscosity decreases the length of the tubes
Higher flow rates can be attained
Viscosity = 1.8 mm2/s, ΣKe = 2
extra

## Slide 111: Tube Diameter for Flow/Dose Controller (Metric tube sizes)
Viscosity = 1.0 mm2/s, ΣKe = 2
extra

## Slide 112: Tube Diameter for Flow/Dose Controller (Metric tube sizes)
It should be possible to achieve flows of 8.7 mL/s using the 5 mm diameter tubes
Viscosity = 1.8 mm2/s, ΣKe = 2
extra

## Slide 113: Design Algorithm
Calculate the maximum flow rate through each available dosing tube diameter that keeps error due to minor losses below 10%.
Calculate the total chemical flow rate that would be required by the treatment system for the maximum chemical dose and the maximum allowable stock concentration.
Calculate the number of dosing tubes required if the tubes flow at maximum capacity (round up)
Calculate the length of dosing tube(s) that correspond to each available tube diameter.
Select the longest dosing tube that is shorter than the maximum tube length allowable based on geometric constraints.
Select the dosing tube diameter, flow rate, and stock concentration corresponding to the selected tube length.
extra
Notes: https://confluence.cornell.edu/download/attachments/77267239/LCDC_ASCE.pdf?version=1&modificationDate=1345649734000

## Slide 114: Making Minor Losses Minor
Eliminate curvature in the dosing tubes; keep them straight and taut (in tension)
Use fittings that have a larger ID than the tube; it will be necessary to stretch the tubing to get it on the larger diameter barbed fittings
extra

## Slide 115: Doser Calibration Steps (whenever the dosing tubes are replaced or elevations are varied)
Make sure the lever is level at zero flow (adjust the length of the cable to the float)
The doser is a linear device and thus when we calibrate it we have ____ adjustments
  __________ the zero flow setting (adjust the height of the constant head tank)
  __________ maximum flow rate (we will adjust this by adjusting the length of the dosing tubes if needed)
2
Intercept
Slope
extra

## Slide 116: Float Valve Head Loss
What orifice diameter is required for a flow of 7.5 mL/s if we don’t want more than 30 cm of head loss?
extra
http://www.cdivalve.com/products/float-valves/pvc-float-valves