## Slide 1: Flocculator Extras

## Slide 2: How do we quantify the turbulence level?
The energy dissipation rate, e, is a measure of the turbulence
It is in the regions of maximum e where the flocs are most likely to break
mW/kg
extra

## Slide 3: Extracting e from Velocity Gradient Design Guideline?
The value of the velocity gradient that was used previously for flocculator design had a range of 20 – 200 s-1
The equivalent range for e is 0.4 – 40 mW/kg
Kinematic viscosity
Velocity gradient
extra
Notes: This is the first of 3 methods to obtain estimates for the energy dissipation rate (traditional G values, traditional velocity values, floc size in a shear environment.

## Slide 4: Extracting eMax from Fluid Velocity Design Guidelines?
Traditional guidelines for velocity are between 0.1 and 0.3 m/s.
Equivalent to of 0.5 to 15 mW/kg
extra

## Slide 5: Design Considerations
Design is dominated by material size and constructability
Channels must be wide enough to be constructible (45 cm)
The material used for flexible plastic baffles is expensive and waste should be minimized

## Slide 6: Vertical vs. Horizontal Flow
For small plants…
  Horizontal flow flocculators are shallow and thus need to be elevated so the water level in the flocculator matches the sedimentation tank
  Vertical flow flocculators take up less space (smaller footprint) because they are deeper
extra
For large plants…
  Horizontal flow can be made as deep as the sedimentation tank and are preferred because they are easier to drain
Notes: Note that these recommendations are the opposite of the recommendations from CEPIS! CEPIS used deep horizontal flow flocculators even for relatively low flow rates (less than 50 L/s). The result is many flocculators with extremely close baffle spacing and resulting inefficient use of flocculator volume because of high variability in energy dissipation rate.

## Slide 7: Vertical vs. Horizontal Revisited
Vertical flow flocculators are somewhat difficult to drain and clean
For large flows, vertical flow flocculators have channels that are wider than they are deep
Why not switch to horizontal flow flocculators for large flows?
Why not use horizontal flow for all flows?
extra

## Slide 8: Horizontal flow for all flows?
5 Lps plant with horizontal flocculator
This is a bad alternative because concrete slab floor, roof, walls, and land are all expensive!!!
extra

## Slide 9: Horizontal Flow Flocculator
Depth of the water is known (W)
Width of the channel is H (unknown)
Use H/S of 3 as a constraint
Solve for S and then finally solve for H
Eliminate H with H/S
extra

## Slide 10: Minimum Flow rate for Horizontal Flocculators given H?
The construction constraint requires that baffles be at least 45 cm (we will use 60 cm) apart (S).
The depth of water is W
Use an H/S of 3 and calculate H
Solve for Q
extra

## Slide 11: Minimum Flow rate for Horizontal Flocculators?
The minimum flow rate for a 2 m deep tank is about 250 L/s
If we build shallower flocculators then we could design horizontal flocculators for lower flow rates (perhaps as low as 50 L/s), but this would increase plant size
Water surface elevations (sed and floc) must match!
So… don’t expect to see any AguaClara horizontal flocculators
extra

## Slide 12: And More Details
How will we fill or drain the flocculator?
What force must the baffles be able to withstand?
  Polycarbonate baffles
  Ferrocement baffles
extra

## Slide 13: Small Drain Ports at the bottom of the lower baffles?
The ports would have a smaller size than the space between baffles
The energy dissipation rate in the jet that flows through the ports will be higher than the energy dissipation rate produced by the baffles
Preliminary evidence from the AguaClara plant at Marcala, Honduras suggests that this approach works well and can still produce low residual turbidity
extra

## Slide 14: Hydrostatic Force: Vertical flow flocculator
H
S
B
L
S
S
Upper baffles
Lower baffles
W currently use 1.5S above and below the baffles
extra
Notes: Change this image to have 1.5 S

## Slide 15: Hydrostatic Force
Where will the baffle break?
If we make the baffle from 4 plates, what force will the lowest plate have to withstand?
extra

## Slide 16: Hydrostatic Force
extra

## Slide 17: Hydrostatic Force
3413
N
extra

## Slide 18: Pro Uniform Flocculation
Most energy efficient (less head loss) or
Given same amount of energy, lower residence time!
Unlikely that the higher shear levels would result in significant changes in floc density or strength
Easier to build
Until we have solid evidence that tapered is better we will use a constant e
extra

## Slide 19: Smallest Turbulent Flow Flocculator (analysis for lab flocculator)
Substitute W=S and eliminate H. Then solve for Q
This is a fundamental equation showing energy dissipation is proportional to velocity cubed
extra

## Slide 20: Add Reynolds constraint
Solve for S to get minimum S given Reynolds constraint
extra

## Slide 21: Minimum Turbulent Flow Flocculation
The minimum flow for a turbulent flow reactor is about 110 mL/s. The minimum S is 3.66 cm
Combine equation for Q and S to get Q as function of Re.
extra

## Slide 22: Get equation for Spacing as function of head loss

## Slide 23: Find ae as function of head loss

## Slide 24: Find residence time as function of Head Loss

## Slide 25: Plan View Area as a function of head loss

## Slide 26: Cost of floc baffles and walls due to head loss
Floc tank walls
baffles
I assume optimal design has S=W

## Slide 27: Cost as function of head loss

## Slide 28: Optimal head loss for a flocculator given 70 m^2/3 collision potential
Notes: See file Optimal Energy Dissipation rate minimum reactor volume
Of course, this is a function of our cost estimates.

## Slide 29: Optimal average and maximum energy dissipation rates
This suggests increasing the maximum energy dissipation rate to about 50 mW/kg, but if we can improve H/S, then we will want to use a lower energy dissipation rate.
Notes: This analysis was done before making the H/S ratio optimal for all designs.

## Slide 30: Optimal velocity gradient
The velocity gradient based on the average energy dissipation rate is in the conventional range of 20 to 180/s

## Slide 31: Head loss

## Slide 32: What is the cost ratio?
Express cost as a wall or ceiling or slab area.
Then cost per plan view area can be approximated as area per plan view area. This assumes that roof, slab, plant walls, and tank walls all have the same cost per unit area.
Cost per plan view area is due to slab and roof and tank walls. Slab and roof are order 2 if expressed as area of slab and roof per area of flocculator.
Tank wall area is H.Floc/W.Floc
Cost per head loss is due to elevation of entrance tank and taller exterior walls of plant
Walls are 4*square root of plant area

## Slide 33: Can I find Q where H/S is at transition?
Use optimal head loss for Small H/S

## Slide 34: As flow increases
H/S>5 and narrow W.Floc
H/S=5 as W.Floc increases to

## Slide 35: Starting from Max EDR
BOD of max EDR
Calculate residence time, head loss and reactor volume
Select channel width based on reactor volume, depth, length, and odd or even number of channels

## Slide 36: Starting from Average EDR
BOD of max EDR
Calculate residence time, head loss and reactor volume
Select channel width based on reactor volume, depth, length, and odd or even number of channels
Set and solve for W
Need an algorithm to solve for

## Slide 37: Find maximum H given minimum W

## Slide 38: Find min Q that doesn’t require obstacles
Use min W and max H/S of 5 to get minimum Q below which obstacles are needed

## Slide 39: Find Max Q for vertical flow flocculator
Use max W and min H/S of 3 to get maximum Q for vertical flow flocculator