## Slide 1: Filtration Theory
On removing little particles with big particles

## Slide 2: Filtration Outline
Sand Filters
  Slow sand (SSF)
  Rough Gravel (RGF)
  Dynamic Gravel (DGF)
  Rapid (RSF)
  Stacked Rapid (StaRS)
Range of applicability
Net Velocity
Hydraulics
Particle Capture theory
  Transport
  Dimensional Analysis
  Model predictions
Methods to improve performance

## Slide 3: Categorizing Filters
Surface filtration (example – membrane filters)
  Particles to be removed are larger than the pore size
  Clog rapidly and large piezometric head required
Depth filtration (not well understood)
  Particles to be removed may be much smaller than the pore size
  Require collisions and attachment
  Can handle more solids before developing excessive head loss
  Filtration model coming…
Our focus here
Require more energy

## Slide 4: Depth Filtration Technologies
Slow (Filters→English→Slow sand→“Biosand”)
  First filters used for municipal water treatment
  Were unable to treat the turbid waters of the Ohio and Mississippi Rivers
  Can be used after rough gravel filters to extend range
Rapid (Mechanical→American→Rapid sand)
  Used in Conventional Water Treatment Facilities
  Used after flocculation and sedimentation
  High flow rates→clog 12 – 90 hr→hydraulic cleaning
Stacked Rapid Sand (StaRS)
  6 x smaller than rapid sand and self backwashing
“Biosand” is a misnomer based on a misunderstanding of SSF mechanisms. The preferred term is intermittent SSF (ISSF)
backwash
scrape
Notes: If you have water in a muddy river and you can only use 2 processes for treatment prior to chlorination, which processes would you choose?

## Slide 5: Filter range of applicability The “if it is dirty, filter it” Myth
1000
NTU
1
10
100
SSF
RSF+
StaRS+
With a floc blanket to extend range
Drawings not to scale!
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf for info on SSF and multistage

## Slide 6: Combining Rapid Sand Filtration and pretreatment
Conventional: Coagulation – Flocculation – Sedimentation – Filtration
  Able to treat very high turbidities because filter is the polishing step
  Effluent from sedimentation should be less than 2 NTU
Direct: Coagulation - Filtration
  An option if raw water turbidity is always low
  less than 5 NTU

## Slide 7: Slow Sand Filtration
First filters to be used on a widespread basis
Fine sand with an effective size of 0.2 mm
Low flow rates (0.03-0.12 mm/s)
Schmutzdecke (_____ ____) forms on top of the filter
  causes high head loss
  must be removed periodically
Used without coagulation/flocculation!
Turbidity should always be less than 10 NTU with a lower average to prevent rapid clogging
filter cake
Compare with sedimentation
Notes: See page 8.77 in Water Quality and Treatment: A Handbook of Community Water Supplies. Fifth edition.
This is the default technology that has been widely touted as the best option for the global south. However failures and abandonment are common.

## Slide 8
Slow Sand Filter
Notes: Part of a multiple stage filtration plant in San Pedro de Tutule, Honduras.

## Slide 9: Multistage Filtration
Another option for communities using surface waters
Uses no coagulants (if lucky)
Gravel roughing filters
Polished with slow sand filters
Large capital costs for construction
No coagulant costs
Labor intensive operation
Notes: http://www.atypon-link.com/TELF/doi/pdf/10.1680/wama.157.3.143.46664

## Slide 10: Multiple Stage Filtration
Dynamic
DGF
Rough
RGF
Slow
SSF
Disinfection
Clogs and shuts down plant during high turbidity event
Reduces turbidity so SSF doesn’t clog so fast

## Slide 11: Assembling Multiple Stage Filters
Notes: San Pedro de Tutle FIME plants

## Slide 12
Notes: San Pedro de Tutle FIME plants

## Slide 13
Dynamic Filter
Roughing
Slow Sand

## Slide 14: Jesus de Otoro, Honduras: Dynamic Filters

## Slide 15: Multiple Stage Filtration Options for pretreatment for SSF
Filters in series with different size media in each filter
Dynamic filter (clogs to shutdown plant)
Up flow gravel filter with multiple layers
Best option here is dynamic + Up flow with layers
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf
See section 4.3 for hint that the drainage system is the piece that requires further research. This suggests that they may still be having difficulty cleaning the sediment from these filters. Note that these filters are not easily disassembled for maintenance and thus do not meet the specifications for easy maintenance required for AguaClara plants.

## Slide 16: Up flow Roughing filter
0.08 to 0.17 mm/s
Turbidity removal is between 50% and 90%
D = 19 - 25 mm
D = 13 - 19 mm
D = 6 - 13 mm
D = 3 - 6 mm
D = 1.6 – 3 mm
overflow
From dynamic filter
Wash water
Rapid opening wash valve
Cap to prevent air entrance during washing
Exit chamber
Effluent
Manifold system
Cleaning, Impossible fittings, Maintenance, Water exit?
2 m long
5.5 mm/s during wash
50x
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf Figure 9.1

## Slide 17: First iteration of covering a roughing filter…
Covered to reduce growth of algae. What is the next logical step?
Notes: https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf

## Slide 18: System Comparison: Multistage vs. AguaClara water treatment
Multistage has more expensive hardware (many large valves) and requires 10 to 20 times more land area
Multistage doesn’t use coagulants
Multistage performs poorly with turbid water
When might multistage be better than AguaClara?

## Slide 19: Rapid Sand Filter (Conventional US Treatment)
Sand
Gravel
Influent
Drain
Effluent
Wash water
Anthracite
Size
(mm)
0.70
0.45 - 0.55
5 - 60
Specific
Gravity
1.6
2.65
2.65
Depth
(cm)
30
45
45

## Slide 20: Rapid Sand Filter Design
Filter media
  silica sand and anthracite coal
  non-uniform media will stratify with _______ particles at the top
Filtration approach velocities
  0.7 – 2.8 mm/s
Backwash approach velocities
  set to obtain a bed porosity, f, of 0.65 to 0.70
  Fluidized bed
smaller
Similar in size to AguaClara Sed (1 mm/s)
Does water speed up or slow down when it enters the sand?

## Slide 21: Backwash (Fluidized Bed)
Sand
Gravel
Influent
Drain
Effluent
Wash water
Anthracite
Wash water is treated water!
WHY?
Only clean water should ever be on effluent side of filter!
Notes: https://www.youtube.com/watch?v=9tqk2cFDi5o#t=226

## Slide 22: Net Velocity Concept for estimating plant size
Use this velocity to determine approximate total unit process area.
Similar approach for sizing AguaClara facility for comparison

## Slide 23
Filter type | Velocity (mm/s) | Cleaning | Max (NTU) | pC* | Area (m2) for 1 L/s
Dynamic | 0.4 |  |  | 0 | 2.5
Roughing1 | 0.17 | 5.5 mm/s downflow |  | 0.52 | 5.9
Slow | 0.04 | Scrape surface | 10 | 0.82 | 25
Multistage | 0.033 |  | 1004 | 1.3 | 33.4
Rapid | 0.7 – 2.8 | 11 mm/s backwash | 55 | 1 | 0.55
Entrance | 8 |  |  |  | 0.125
Flocculation | 4 |  |  |  | 0.25
Sedimentation | 1 |  |  | 2.5 | 1
Floc Hopper | 5 |  |  |  | 0.2
Stacked Rapid | 1.8 x 6 | 11 mm/s backwash | 36 | 16 | 0.093
AguaClara | 0.63 |  | 10005 | 3.5 | 1.67
1 Roughing is up flow in layers
2 Based on table 5.7 https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf
3 Net velocity for scaling total plan view area of facility.
4 This assumes a target of 5 NTU in the effluent
5 Assumes a target of 0.3 NTU in the effluent (based on performance of the Atima plant)
6 Data from Tamara.
The 32 L/s plant at San Nicolas has 5.5 m2 per L/s (includes chemical room, bathroom, office , etc.)
Notes: Based on table 5.7 of https://confluence.cornell.edu/download/attachments/90755680/FiME+CINARA.pdf
Note that areas don’t include controls, entrance tanks, walkways, etc.
Flocculator is 2 m deep and residence time is about 500 s.
The 32 L/s plant at San Nicolas has 5.5 m^2 per L/s

## Slide 24: Filter Hydraulics
Porosity
Sand size definitions
Clean bed head loss estimates
Backwash requirements
Low flow design challenges: the backwash dilemma

## Slide 25: Porosity
volume of voids
total volume
Example: 1 m3 of dry aquifer material weighed 1600 Kg. The aquifer material was then saturated with water and found to weigh 2000 Kg.
What is the porosity of the aquifer material?
What is the bulk density of the aquifer material?
What is the density of the aquifer material?
0.4
1600 kg/m3
2700 kg/m3

## Slide 26: Porosity
Which will have the greatest porosity?
  1 µm diameter clay
  0.2 mm diameter sand
  1 cm diameter gravel
You have been given 100 kg each of clay, sand and gravel
  What could you do to create the lowest porosity?
100 kg gravel, 100*0.4/0.6 kg sand, 100*(0.4/0.6)2 kg clay
Notes: 100 kg, 67 kg, 44 kg

## Slide 27: Expanded Bed Porosity
Pore volume + volume above bed = Expanded bed pore volume
Total expanded volume
Filter expansion ratio
Backwash porosity
Now we can relate porosity and filter expansion ratio
Notes: Sand fraction * height of sand is conserved!

## Slide 28: Sand Grading
Effective Size
  D10 - sieve size that 10% by mass of the sand passes through
  Used for filter particle removal modeling
D60 – sieve size that 60% by mass of the sand passes through
  Used for hydraulic modeling
Uniformity Coefficient = D60/D10

## Slide 29: Clean Bed Head Loss (Karmen Kozeny)
Kozeny constant
Approximately 5 for most filtration conditions
Porosity (0.4 for uniform size media)
Head loss
Flow path length (filter bed depth)
Approach velocity
Sand diameter
Kinematic viscosity
Assumes laminar flow and is valid up to Re of 6
Hagen Poiseuille
Notes: Karmen Kozeny valid up to Re of 6
Page 8.10 in Water Quality and Treatment: A Handbook of Community Water Supplies. Fifth edition.

## Slide 30: Backwash Requirements – Head Loss (force balance)
For FiSand=0.4 and rSand=2650 kg/m3
=
Weight of water/Filter area
Weight of sand/Filter area
Notes: The pressure drop times the filter area is equal to the buoyant weight of the sand grains.

## Slide 31: What does this analysis miss?
Sand bed may first lift as a unit and then fall into the fluidized state
Wall shear (scale effect!!!!) and embedded pipes may prevent bed lift (or require more force than our simple force analysis suggests)
Sand will stratify if there is even a small range of sizes: Backwash velocity must be sufficient to fluidized the largest sand
Backwash initiation requires more study

## Slide 32: Backwash Requirements – Flow Rate
Kozeny
Set them equal
Backwash Head Loss
Minimum approach velocity required to fluidize bed
Notes: Using D60 might not be conservative enough.

## Slide 33: Backwash Velocity
0.45 mm E.S. with 1.65 U.C. = D60 0.72 mm
Fluidize at 5 mm/s
30% bed expansion at 12 mm/s
PFiBw is expanded bed depth over settled bed depth
(Effective size)
Notes: This seems a bit of a stretch because we are starting with pipe flow equations. It might be better to switch to sphere sedimentation equations.
Karmen Kozeny valid up to Re of 6
Page 8.10 in Water Quality and Treatment: A Handbook of Community Water Supplies. Fifth edition.

## Slide 34: Backwash sand bed stratification
Suppose the sand stratifies in the filter bed during backwash and suppose that 10% of the bed is smaller than 0.4 mm and 10% of the sand is bigger than 0.8 mm
What is the ratio of fluidization velocity for the top of the sand bed to the fluidization velocity for the bottom of the sand bed?
Notes: Sand at top has a diameter that is ½ of the sand at the bottom. Therefore velocity to fluidize the top will be ¼ of the velocity required to fluidize the bottom. Thus seeing sand fluidize at the top of a filter bed does not guarantee that it is fluidized at the bottom.

## Slide 35: The Backwash Dilemma
Backwash velocity >> filtration velocity
Backwash water must be clean water
Backwash water sources?
  Pump it from clearwell
  Set of filters working in parallel to backwash one filter
  Filtered water stored at adequate elevation

## Slide 36: Rapid Sand Filtration Battery: Backwash without pumps
https://confluence.cornell.edu/display/AGUACLARA/Santa+Rosa+de+Copan
What are these two valves controlling? Reverse engineer the universe!

## Slide 37: The Low Flow Challenge: Filter Set
Assume plant flow is 6 L/s, Filtration velocity is 1.8 mm/s and backwash velocity is 9 mm/s and that a set of filters will backwash one filter
How many filters?
Total filter area?
What happens if the plant is operating at half capacity (drought conditions)?
Need filters to be smaller to be able to backwash one!

## Slide 38: Store filter water?
Try two filters and recalculate
Require a large tank and the tank must be shallow to keep filters from being really deep.
  Filters need to be able to load the tank during filtration and then take water from the tank during backwash. This is accomplished by having the filter water level VERY high during filtration and low during backwash
  Requires more area than sed tanks!
Notes: Fails the ridiculous test as named by Mickey Adelman
  Identify filtration head loss and backwash head loss

## Slide 39: The Low Flow Challenge
Requiring 6 filter boxes for a small plant is too costly and difficult to construct and maintain.
Storing filtered water requires a storage tank with a Vup less than the entire AguaClara plant!!!
If we rule out the pump option, then we have no good options…

## Slide 40: Why is this difficult?
The backwash dilemma is due to the big difference between backwash flow rates and filtration flow rates
6 filters are required if backwash velocity is 5 times the filtration velocity
If we could get those velocities to be similar or equal, then we wouldn’t need a set of 6 filters
Invention time
Notes: Brainstorm ways to get those velocities to be similar!
Decrease media density so it fluidizes at a lower velocity
Decrease media diameter so it fluidizes at a lower velocity (but that will increase head loss during filtration mode too)
Make a more compact filter. (filter in parallel, backwash in series!)

## Slide 41: Geometric Trick: Stacked Rapid Sand Filter (StaRS)
Instead of 6 filters side by side, stack them up!
Reduce backwash water volume by factor of number of layers
Notes: Optimal number of layers is a function of backwash requirements and optimal filtration velocity. We are using shallower filter beds than conventionally used and thus filter performance is expected to be poorer.

## Slide 42: Water Source for Backwash
Tradition says Filtered Water
Why not use Settled water?
Public Health trade off?
  Filter to waste after backwash is required in any case due to contamination of manifold tubing
  Use of settled water significantly simplifies the system
Same flow rate and water source during filtration and backwash!!!!
Eliminate empty clearwell failure mode

## Slide 43: Water waste
The amount of water wasted from each unit process is determined by the average solids concentration of wasted water and the solids concentration entering the process.
The goal is to have the wasted water have as high of a solids concentration as possible
Backwash water is very dilute compared with the solids concentration from the floc hoppers
Backwash water can be reprocessed, but that requires a pump (a good option to explore for dry season water saving)
Notes: Estimate of backwash waste from Water Quality and Treatment: A Handbook of Community Water Supplies. 5th ed. AWWA

## Slide 44: StaRS Filter Fabrication
San Matías construction
Backwash operation

## Slide 45: Pipe Gallery (San Nicolas)

## Slide 46: Eliminating 7 big valves: One valve control of a StaRS Filter
The following slides illustrate the method of using a siphon tube to initiate backwash
The filter animation only shows how the siphon will work. It doesn’t show how the inlet and outlet manifolds will be controlled
The Filter Inlet and Outlet control boxes will be designed so that water level changes* during backwash will cause all of the manifold pipes to be hydraulically separated and thus no valves will be required to turn off the inlet or outlet pipes
Notes: *This will require a slight increase in the depth of the filter to accommodate a larger change in water levels between filtration and backwash

## Slide 47: Begin Filtration

## Slide 48: Begin Backwash
Notes: Need to analyze the beginning of the siphon right after the air pressure is equalized with atmospheric pressure. It appears that we may need the height of water above the top of the siphon tube to equal the depth of submergence of the end of the siphon to initiate flow through the siphon

## Slide 49: End Backwash

## Slide 50: The big flush
Patent US2017263 - FLUSHING APPARATUS - Google Patents
Notes: Patent US2017263 - FLUSHING APPARATUS - Google Patents

## Slide 51
End Backwash cycle
What is the head loss in the sand bed between an inlet and an outlet?
What is the head loss through the sand bed + plumbing?
Constraints on depth of water in inlet box during backwash?
Notes: Backwash water level must be high enough to not pull air into the filter and low enough to not flow into the other inlets.

## Slide 52: Head loss between manifolds Assume expansion ratio of 1.3
Find depth of settled sand in 20 cm of expanded sand
Expanded depth (20 cm)
Settled depth
This is head loss per 20 cm of expanded bed!

## Slide 53
Begin Filtration cycle
Outlet box
Total filter head loss
Inlet plumbing head loss

## Slide 54
End Filtration cycle
Outlet box
What causes water to flow through the filter bed?
____________________________
differences in piezometric head
Total filter head loss
Notes: Does gravity matter?
Apply the energy equation.
What must be true about the head loss for each parallel path?
What is the ratio of flows that the bottom inlet must be able to handle? If the head loss in the bottom inlet system is 10 cm during filtration, then what would it be during backwash?
What does this say about the head loss in the inlet system during filtration?
What must be true about the head loss in the pipe inlets in order to get uniform flow distribution?

## Slide 55
Backwash cycle

## Slide 59: How does water flow through StaRS Filters?
Water flows in direction of decreasing piezometric head

## Slide 60: Filter Design Constraints
Spacing between inlet pipes (or outlet pipes) must be small compared with layer depth
Filter should be able to be backwashed at the beginning of filtration cycle if needed
All inlets and outlets (except bottom inlet) must be high and dry during backwash
Kinetic energy in trunk lines and inlet/outlet pipes must be less than 10% of the clean bed head loss to achieve uniform flow distribution in sand bed*
* Edge of knowledge
Notes: See manifold notes for justification for kinetic energy guide.

## Slide 61
10 cm + Pipe OD + 10 cm
20 cm
Max and min filtration water levels
Inlet
Outlet
Notes: This doesn’t have every last detail included (such as head loss over the backwash weir, but it is close.
How could you measure expansion ratio?

## Slide 62: EStaRS and OStaRS Enclosed vs. Open
Fabrication becomes difficult with filter dimensions less than 1 m x 1m
Minimum OStaRS flow rate is about 8 L/s
EStaRS doesn’t require excavation because filter is operated under vacuum for backwash

## Slide 63: StaRS Backwash Advantage
Where does the water come from that fills the filter box after the siphon is broken at the end of backwash?
Where does the water come from that slowly fills up the filter box during a filtration run?
Unlike RSF the backwash water above the StaRS bed does not pass through the sand during filtration

## Slide 64: StaRS Challenges
Inlet slotted pipes clog
  2015 replaced with
Water level changes above sand result in unnecessary water waste
Could we replace Outlet slotted pipes?

## Slide 65: Particle Removal Mechanisms in Filters
Transport to a surface
Attachment
Molecular diffusion
Inertia
Gravity
Interception
Straining
collector
Polar coagulant
Gravity

## Slide 66: San Matías Performance
Average pC* for the filter is 0.8

## Slide 67: RSF Performance
Data from Cornell University Water Filtration Plant. They were using alum at this time.
Notes: Data from Cornell University Water Filtration Plant. They were using alum at this time.

## Slide 68
Very steep failure
Lucinda Li, Theresa Chu, Jonathan Harris, Mythri Krishnamoorthysujatha, Rose Linehan, William H. Pennock
Notes: Lucinda Li, Theresa Chu, Jonathan Harris, Mythri Krishnamoorthysujatha, Rose Linehan, William H. Pennock

## Slide 69: Active filtration zone slowly moves down through the filter
Effluent Turbidity
NTU
Time

## Slide 70: Active Filtration zone
NTU
Time
Active Filtration zone
Filtration improves while loaded zone expands and clean zone shrinks
Therefore particle removal is better in loaded zone than in clean zone or flocculation helps!
Active filtration zone breakthrough
(big flocs get to the bottom of the filter first)
Backwash debris
Loaded zone
Clean zone

## Slide 71: Head loss in Filters is close to linear before breakthrough
Breakthrough

## Slide 72: Head loss and fraction loaded are increasing linearly together
Head loss continues to increase after the active zone reaches the filter effluent
Head loss increase becomes nonlinear with time after the active zone reaches the filter effluent

## Slide 73: What do we know?
Flocs occupy a few percent of the void volume in a loaded filter
  Insufficient floc volume to uniformly decrease void volume and increase fluid velocity, shear, and major losses
Head loss is close to linear with time
Clean bed filtration models
  Removal is primarily due to interception
  Sedimentation may be important too

## Slide 74: Interception occurs where streamlines converge
Particles are deposited at the constriction
The biggest part of the filter pore remains empty!
Big particles can’t attach to partially filled restrictions
No removal by interception in straight tube

## Slide 75: StaRS Optimization
Sand Diameter – smaller diameter is more efficient at particle capture, requires a lower backwash velocity and thus a lower filtration velocity could be used
Layer height – filter box rapidly becomes very deep to accommodate deep layers
Slot width – wider slots would take longer to clog
More research required to improve the design
Notes: Perhaps filter media size has also evolved to be large enough to cause sufficient violence during backwash to remove particles. Thus it is possible that if we try a smaller filter media size that the filter won’t clean well.

## Slide 77: Conclusions…
Many different filtration technologies are available
Filters are well suited for taking clean water and making it cleaner. They are not a good choice for treating very turbid surface waters
Pretreat using flocculation/floc blanket/plate (or tube) settlers

## Slide 78: …Conclusions…
Filters could remove particles more efficiently if the _________ efficiency were increased
StaRS 3 main advantages over RSF
  ____________
  ______________________________________
  Single valve control
RSF (and StaRS) require pretreatment with coagulant
Self backwashing (no pumps)
Smaller filter area required
attachment

## Slide 79: …Conclusions
RSF have pC* of 1 to 1.5 under normal conditions (max influent turbidity is about 5 NTU)
StaRS have pC* of 1 (preliminary data)
SSF have pC* of 1 to 1.5, but they perform poorly if the water contains much colloidal clay
Sand Filters CAN NOT treat turbid water
Notes: We need to update the StaRS pC*

## Slide 80: References
Tufenkji, N. and M. Elimelech (2004). "Correlation equation for predicting single-collector efficiency in physicochemical filtration in saturated porous media." Environmental-Science-and-Technology 38(2): 529-536.
Cushing, R. S. and D. F. Lawler (1998). "Depth Filtration: Fundamental Investigation through Three-Dimensional Trajectory Analysis." Environmental Science and Technology 32(23): 3793 -3801.
Tobiason, J. E. and C. R. O'Melia (1988). "Physicochemical Aspects of Particle Removal in Depth Filtration." Journal American Water Works Association 80(12): 54-64.
Yao, K.-M., M. T. Habibian, et al. (1971). "Water and Waste Water Filtration: Concepts and Applications." Environmental Science and Technology 5(11): 1105.
M.A. Elliott*, C.E. Stauber, F. Koksal, K.R. Liang, D.K. Huslage, F.A. DiGiano, M.D. Sobsey. (2006) The operation, flow conditions and microbial reductions of an intermittently operated, household-scale slow sand filter
Enhanced Filter Performance by Fluidized-Bed Pretreatment with Al(OH)3(am): Observations and Model Simulation Po-Hsun Lin, Leonard W. Lion, and Monroe L. Weber-Shirk. Journal of Environmental Engineering 1, 389 (2011).

## Slide 81: Filtration Performance: Dimensional Analysis
What is the parameter we are interested in measuring? _________________
How could we make performance dimensionless? ____________
What are the important forces?
Effluent concentration
C/C0 or pC*
Inertia
Thermal
Sticky? (a – attachment efficiency)
Viscous
Need to create dimensionless force ratios!
Gravitational
transport
attachment
Performance = f(forces, geometry)

## Slide 82: What is the Reynolds number for filtration flow?
What are the possible length scales?
  Void size (collector size) 0.7 mm in RSF
  Particle size
Velocities
  VFi varies between 0.03 mm/s (SSF) and 2.8 mm/s (RSF)
Take the largest length scale and highest velocity to find max Re
Flow through SSF, RSF, and StaRS is laminar during filtration

## Slide 83: Choose viscosity!
In Fluid Mechanics inertia is a significant “force” for most problems
In porous media filtration viscosity is more important that inertia.
We will use viscosity as the repeating parameter and get a different set of dimensionless force ratios
Inertia
Gravitational
Viscous
Thermal
Viscous

## Slide 84: Dimensionless Force Ratios
Reynolds Number
Froude Number
Weber Number
Mach Number
Pressure/Drag Coefficients
  (dependent parameters that we measure experimentally)

## Slide 85: Gravity
v
pore
Gravity only helps when the streamline has a _________ component.
horizontal
velocities
forces
Use this definition

## Slide 86: Diffusion (Brownian Motion)
kB=1.38 x 10-23 J/°K
T = absolute temperature
v
pore
dc is diameter of the collector
Diffusion velocity is high when the particle diameter is ________.
small

## Slide 87: Geometric Parameters
What are the length scales that are related to particle capture by a filter?
  ______________
  __________________________
  ______________
  Porosity (void volume/filter volume) ()
Create dimensionless groups
  Choose the repeating length ________
Filter depth (z)
Collector diameter (media size) (dc)
Particle diameter (dp)
(dc)
Number of collectors!
Definition used in model

## Slide 88: Write the functional relationship
Length ratios
Force ratios
If we double depth of filter what does pC* do? ___________
doubles
How do we get more detail on this functional relationship?
Empirical measurements
Numerical models
a=Attachment efficiency

## Slide 89: Filtration Model Limitations
Filtration model is really a “clean bed” model
  Likely not able to explain performance during a filter run
  Doesn’t account for pore filling
pC* is proportional to depth (not consistent with observations of operating filters)
pC* is independent of influent particle concentration (not consistent with observations of operating filters)
Influent particle size distribution is likely very important and may control pC* for real filters

## Slide 90: Stacked Rapid Sand Filter predicted performance for biological particle
Not very good at removing particles that haven’t been flocculated
Notes: Interception is very important
Lousy at removing pathogens if they haven’t been flocculated
A 0.1mm particle has a pC* of 100!!!!!!!!!!
Either particles haven’t be
http://designserver.cee.cornell.edu/aguaclaracode/FiltrationModel.xmcden flocculated or attachment is poor

## Slide 91: Stacked Rapid Sand Filter predicted performance for inorganic particle
What is the density of particles that are being removed in a StaRS Filter?
Notes: Gravity is very important for these dense particles
http://designserver.cee.cornell.edu/aguaclaracode/FiltrationModel.xmcd

## Slide 92: StaRS and Fractal Flocs predicted performance
The filtration model combined with the fractal flocculation model suggests that filtration is dominated by interception for all particles sizes for approach velocities above about 1 mm/s.
Notes: http://designserver.cee.cornell.edu/aguaclaracode/FiltrationModel.xmcd
I see this as a big mystery. If a sticky clay particle can’t attach to a floc in a floc blanket, then is it possible for a clay particle to attach to a sand grain? It would seem that interception (the flocculation mechanism) might not be a viable mechanism for attaching little particles to big particles. So perhaps this is actually about sedimentation!

## Slide 93: Filter as Flocculator?
Head loss of 40 cm
Residence time of 44 s
Gq of 13,000!
Filter provides one last chance for flocculation especially after head loss increases

## Slide 94: Small particles slip through a small restriction
The vast majority of small particles slide right through a constriction
Constriction diameter

## Slide 95: A series of restrictions takes a toll on even the small particles
If we assume complete mixing in each pore then the probability of slipping through N pores is
Number of pores to get 90% removal
Number of pores to get a target fraction remaining
How much mixing happens in each pore? Is the outer ring of fluid refreshed?

## Slide 96: Tiny (or slippery) bad guys sneak through all the security
Some small particles escape flocculation, floc blanket, plate settlers, and filter
  Because they are small (not likely because effluent turbidity stayed the same when flow rate was decreased in a filter)
  Or because a few particles aren’t coated with nanoparticles (they are slippery)
    Because they never got enough nanoparticles of coagulant
    Or the nanoparticles were sheared off during
      Failed attachments
      Breakup
How could we determine if it is small size or lack of nanoparticles or something else?

## Slide 97: What could cause slippery particles (with too few nanoparticles)?
Pulsing peristaltic pumps
Statistical variability given small number of nanoparticles per clay
Nanoparticles removed during unsuccessful collisions (this could occur during flocculation and/or during filtration

## Slide 98: Head loss in filters is close to linear before breakthrough
Why does increased coagulant dose result in earlier failure?
  Higher coagulant dose results in bigger flocs and fewer small flocs
  Thus failure must be from big flocs
  Big flocs can’t deposit in partially formed restrictions
Why is head loss accumulation faster with more coagulant?
  More coagulant = bigger flocs and bigger flocs are less dense/occupy more volume

## Slide 99: Flocs on their way to the filter
We use weirs and free fall to ensure that the flow is divided equally between filters and is not affected by the head loss of the filter
The elevation drop into the entrance box is approximately 0.4 m.
Velocity is 2.8 m/s
If we assume a 1 cm thick jet of water then the energy dissipation rate is 140 W/kg
The max diameter of a floc is thus 14 mm

## Slide 100: Floc removal efficiency increases rapidly with floc size
Perhaps filter performance is largely controlled by the size distribution of influent flocs. We need particle size distribution entering and exiting the filter
Individual clay particles would be hard to capture
20 cm bed of 0.5 mm sand
Notes: http://designserver.cee.cornell.edu/aguaclaracode/FiltrationModel.xmcd

## Slide 101: Filtration of mixed particle sizes
Filtration model
Definition of pC* where i represents the bins containing different size fractions
Mixtures produce nonlinear relationship between pC* and filter bed depth
Effluent concentration of each size class

## Slide 102: Interception
DE Expanded diameter (big pore)
DC Contracted diameter
DP Particle diameter
What fraction of the particles slip through?
DE
DC
DP

## Slide 103: Methods to improve Rapid Sand Filter Performance
Increase attachment efficiency
Flocculate particles to make them larger
Add coagulant to the filter influent to make the filter media and previously captured particles stickier (50 mg/L of Al has been shown to be effective at Cornell Water Treatment Plant)
Po-Hsun Lin 2011
Notes: Po-Hsun Lin

## Slide 104: Flocculation may be a significant mechanism inside a filter
The equations are simplified major losses in a clean filter bed
Flocculation increases as head loss increases (another reason for this)
NTU
Time

## Slide 105: StaRS Design Guidelines
Settled water is divided evenly between filters that are in filtration mode
  Weir into entrance box
    need to eliminate air entrainment problem
Backwash filter gets design flow
Each filter has an overflow box
Filtered water flows over a weir into a box taking water to the distribution tank

## Slide 106: Siphon Geometry for Air trap
What must be true for the air in the siphon air trap?
  Mass of air must be conserved
    Volume of air is NOT conserved
  Pressure in the air is independent of elevation
    Depth of “submergence” (hydrostatic pressure) must be the same at both ends of the siphon!
What relationship can we use to final volume of air given initial volume of air?
  PV=nRT

## Slide 107
L10
L30
L2
H1
H2
H1
H3
H1
H2
H1
H3
Siphon Geometry
What determines how much air we trap?
What happens as head loss increases?
Success requires two things
1. Start backwash whenever desired.
2. Prevent backwash from starting.
Notes: As head loss increases H1 increases. That means that some water must flow out of the end of the siphon pipe. That means that the water level in the vertical section of pipe inside the filter box must rise too! At some point we will get H1=H3 and the siphon will start flowing!

## Slide 108: Siphon Geometry for Air trap
0
1

## Slide 109: Maximum water level that can be held by siphon
Failure mode is when H1=H3 Set H1=H3, then solve for H3
This is the maximum value of H3