## Slide 1: Prelim 2 Review M-F of next week
With a focus on Flocculation and Sedimentation and beginning of Filtration
12 points - 3 multiple choice
18 points – 6 short answer
70 points – design challenges

## Slide 2: Who can I talk with about what?
No conversations (social media, discussion boards, etc.) with anyone* about CEE 4540 between Monday class and Friday class
  *Except in class!
  *You can ask questions to Juan or Monroe (email or in person)

## Slide 3: Flocculator Equation Summary
Equations for average energy dissipation rate
Baffle spacing
Maximum distance between expansions to ensure relatively uniform velocity gradients
Minimum channel width to prevent
Distance between flow expansions

## Slide 4: AguaClara Sedimentation Tank
Exit Channel
Entrance Channel
Launder
Inlet Manifold
Plate Settlers
Diffusers
Sed Tank Drain
Floc Weir
Floc Hopper
Floc Hopper Drain (to remove sludge)
Dump poorly flocculated water channel
Exit Weir that controls water levels all the way back to the next free fall (LFOM!)
Notes: Exercise: Tell the story of the journey of a large floc, a small floc, a rouge loner clay particle, and of a water molecule as each travels through this sedimentation tank.

## Slide 5: AguaClara Sed Tank Geometry
Notes: How does the operator drain sludge from the floc hopper (which valve)?

## Slide 6: AguaClara Sed Tank Geometry
Notes: Why do the PVC pipes that create the floc baffle modules extend all the way to the end wall at the downstream end of the floc tank?
Why is the sed tank inlet channel sloped uphill?
What controls the water level in the sedimentation tank?
What is the water level in the flocculator under the condition of zero flow?
What is in the floc hopper before it begins to fill with flocs?

## Slide 7: How can you drain and then refill a sedimentation tank?
Notes: Why does the plug have a vertical tube? Serves as a handle and an air vent.

## Slide 8: Sedimentation: How do these velocities connect to design?
Settle capture – determines the slowest terminal velocity floc that will settle to a surface
Slide capture – determines the slowest terminal velocity floc that will slide down the plate. Function of velocity gradient at plate settler surface, angle, and floc density
Upflow – set to obtain good performance of the floc blanket (ongoing research)
Terminal – floc property set by maximum energy dissipation rate of the environment it is in AND by the previous collision potential

## Slide 9: Settle Capture Velocity
Which provides better removal of particles, a low settle capture velocity or a high settle capture velocity?
Suppose you keep plate length constant and decrease spacing between plates. What happens to performance and cost?
Could you design a sed tank with a floc blanket without plate settlers?
Notes: Low capture velocity is best to capture smaller particles
Decreasing spacing would decrease capture velocity and increase cost (more plastic)
no. The plate settlers are needed to return small particles to the floc blanket. All flocs with terminal velocities lower than Vup would be carried into the effluent!

## Slide 10: Performance ratio (conventional to plate/tube settlers)
Compare the area on which a particle can be removed
Use a single plate settler to simplify the comparison
a
S
L
Conventional capture area
Plate/tube capture area

## Slide 11: Quiz 11/5/14
__crease the amount of plastic needed for plates
__crease the velocity gradient at the plate
__crease the slide capture velocity
__crease the height of the plate settlers
__crease the head loss through the plate settlers
__crease the Reynolds number for flow between the plates
Decrease the plate settlers spacing (and maintain the same up flow in the sed tank and the same capture velocity)
de
de
same
in
in
in
Notes: d and f

## Slide 12: Sed Questions
What determines the depth of the sedimentation tank?
What happens if you make the sedimentation tank 2 m wide or 50 cm wide?
Why does the flow divide evenly between the sed tanks?
Notes: Add up all the pieces, jet reverser, angled sides, perhaps depth of floc blanket, clear space between floc blanket and plate settlers, plate settlers, effluent manifold.
If you made the sed tank wider the sloped section has to get deeper.
Head loss (primarily in the effluent manifold orifices) forces the water to flow to distribute equally between the parallel paths.
More piezometric head required to drive the water through the parallel paths than there is difference in piezometric head between the paths.

## Slide 13: Anything that makes differences in parallel paths is bad!
Inlet channel
Settled water outlet channel
Inlet manifold
Diffuser exit loss
Launder orifice loss
Floc blanket and plate settlers
Effluent manifold (Launder)
Pressure change from
Flow deceleration and head loss
Battery creates 5 to 10 cm of potential energy to drive the flow
Pressure change from flow acceleration and head loss
Launder exit losses
Flow distribution is a major hydraulic design constraint (see manifolds.pptx)
Notes: We will cover this in manifold hydraulics if we have time. Which resistance is good and improves flow distribution? Which resistance makes flow distribution poor?
Anything that makes differences in parallel paths is bad!

## Slide 14: Flow Distribution
Does high velocity in a sed tank inlet manifold help or hurt flow distribution?
  Why?
If you increase velocity in a manifold what else must you do to maintain uniform flow distribution?
Notes: High velocity in inlet manifold hurts flow distribution because of pressure recovery (increase in Piezometric head toward the downstream end of the manifold)
Must increase the head loss in parallel paths. One option is to increase the velocity of the diffuser exits.

## Slide 15: Floc Hopper Q's:
What is in the floc hopper before it fills with flocs?
Why do flocs flow over the floc hopper weir?
Why does a floc blanket interface slowly rise?
How fast are flocs settling unto the sloped bottom?

## Slide 16: Floc Blanket
Why would a floc blanket not work if AguaClara didn’t use plate settlers?
What mechanisms could explain why a floc blanket reduces the turbidity of the settled water?
Notes: Upflow velocity required for a floc blanket results in significant turbidity above the flow blanket

## Slide 17: Backwash Requirements – Head Loss (force balance)
For eFiSand=0.4 and rSand=2650 kg/m3
=
Weight of water/Filter area
Weight of sand/Filter area
Notes: The pressure drop times the filter area is equal to the buoyant weight of the sand grains.

## Slide 18: Big picture: Prelim question that didn’t make the cut…
An AguaClara plant that includes all of the latest in design innovations (flocculation, floc blanket, floc hopper, plate settlers, stacked rapid sand filter) is built for a community of 15,000 people with a per capita demand of 3 mL/s per person. The facility has 8 sed tanks and 2 filters. During a drought the flow rate through the plant is reduced by 50%. Which unit processes are affected negatively by a reduction in flow rate and what changes in operation would you advise?
Notes: Flocculator might drop some flocs. Can clean the flocculator later.
Floc model predicts the flocculator would perform worse
Inlet channel might drop some flocs. Not a problem.
Floc blanket might collapse. Consider taking some sed tanks off line.
Filters will be fine as long as you can divert all of the flow to one filter to backwash it.