## Slide 1: Prelim 1 Review
Prelim 1 Tuesday October 17
7:30 pm in 318 Phillips

## Slide 2: General Question
Test format: What types of questions should we expect?
  7 multiple choice questions (4 points each)
  Short problems (includes one graph)
How far should we be able to extrapolate beyond what is in the notes?
  You should understand the fundamental concepts and be able to talk about those concepts with your friends
  Algebra and arithmetic are expected

## Slide 3: Python based Prelim
What could fail?
  No communication with other humans during the exam
  No posting questions or answers on the web
  Delete part of the exam by mistake (save a copy with your name in the title as step 1)
How do you minimize risk of failure?
  Save versions
  Also submit a pdf copy. Print the webpage as a pdf (File – print preview, then print as pdf)

## Slide 5: What are examples of major and minor losses?
Major: Caused by shear with the solid surface
  Pipe walls
  Flocculator baffle surfaces (insignificant)
Minor: Flow expansions (analogous to pressure drag)
  Orifice, elbow, valve, any place where flow is expanding!
  KE is converted into 2 things!
Velocity
Shear (wall on fluid)

## Slide 6: Head Loss due to Sudden Expansion
Discharge into a reservoir?__________________
Energy
Momentum
Mass
Loss coefficient = 1
2
2
2
Ke
Ke’
Notes: Emphasize the minor loss coefficient is defined based on some relevant velocity. We can chose either V1 or V2. But the magnitude of the minor loss coefficient is determined by which velocity we use. We need to choose one and be consistent. The velocity that we choose will be a function of convenience. Minor losses are proportional to the square of the velocity. This is true whether the flow is turbulent or laminar!

## Slide 7: The Challenge of Chemical Metering (Hypochlorinator)
What is the simplest representation that captures the fluid mechanics of this system?
Raw water entering distribution tank
Overflow tube
PVC valve
PVC pipe
Access door to distribution tank
Chlorine drip
Chlorine solution
Access door to hypochlorinator tank

## Slide 8: Hole in a bucket (tank drain)
What type of head loss (major or minor)?
What is the equation for those loses?
How would you calculate the initial flow rate given the minor losses?
How does the flow vary with time?
What is the average flow rate while the tank is emptying?
Notes: Minor
Minor loss equation
Solve for V and note that Q=VA
Flow decreases linearly with time
Average Q is ½ of initial Q.

## Slide 9: Hole in a bucket (tank drain)
Case 2, h0=1 m, htank = 1 m, tdesign=4 days

## Slide 10: What happens if raw water temperature drops in a WTP?
Flow measurement
Chemical feed (air temperature?)
Rapid mix
Flocculation
  Head loss through flocculator
  Fluid deformation (Gq)
Sedimentation – prelim 2!
Notes: Flow measurement (no change in minor head loss)
Chemical feed (air temperature?) If stock chemicals chill, then increased viscosity gives lower chemical flow rate.
Rapid mix (both diffusion and fluid deformation will slow down)
Flocculation
  Head loss through flocculator (no change)
  Fluid deformation (Gq) (decrease in G)
Sedimentation (decrease in sedimentation rate)

## Slide 11
H
Open channel supercritical flow
Drop tube
Dosing tubes
Stock Tank of coagulant
Lever
LFOM
Float
Constant head tank
Float valve
Slider
Purge valves
Notes: Why is Q vs depth of water linear for the entrance tank?
Why is Q vs H linear for the coagulant?

## Slide 12
H
Decrease dose

## Slide 13
Increase dose
H

## Slide 14
H
Half flow

## Slide 15
Plant off

## Slide 16
Where is this equipment in the new design?

## Slide 18: Chemical Dose Controller
What is the purpose of CHT?
What is the purpose of the dosing tubes?
What is the design constraint for the maximum flow rate in the dosing tubes?
Why does the flow through the dose controller increase if the plant flow rate increases?

## Slide 19: Head loss, energy dissipation rate, velocity gradient
Use these equations to relate velocity gradient to velocity (and then to flow geometry)

## Slide 20: Energy dissipation rate
e | Equation source | Equation | scale
Ave | Control volume mass momentum energy |  | time over which energy is dissipated
Max | Dimensional analysis |  | Flow dimension

## Slide 21: Maximum Energy Dissipation Rate
Type of expansion | Context |  | Equation
Round jet |  |  | 
Plane jet |  |  | 
Plate |  |  | 
Type of expansion | Context |  | Equation
Round jet |  |  | 
Plane jet |  |  | 
Plate |  |  | 
Rapid mix
Hydraulic flocculator
Mechanical flocculator
0.34
0.225
0.5

## Slide 22: Power and Energy
Energy: Joule = Newton*meter
Power: Watt = Joule/s
Water elevation change in an AguaClara plant is about 2 m. How much energy are we using per kg of water?
If the flow rate is 100 L/s, what is the equivalent power?
Desalination = 1 km, distillation = 250 km
2m*g = 19.6 (m/s)^2 = J/kg
0.1m^3/s*1000kg/m^3*19.6J/kg = 1900 W
Notes: 2m*g = 19.6 (m/s)^2 = J/kg
0.1m^3/s*1000kg/m^3*19.6J/kg = 1.9 kW

## Slide 23: Identify all of the parameters in the Floc Model